Aluminum Honeycomb Raised Floor

Abeite Aluminum Honeycomb Raised Floor is 100% recyclable. Lightweight

aluminum honeycomb as core panel, the top finished with HPL/PVC/Ceramic, etc

covering, galvanized steel sheet or aluminum foil to bottom, the four edges are wrapped

with conductive PVC trims.

| Type: | FS662-2000 |
| --- | --- |
| Finished Floor Height: | 100-2000mm |
| Panel Size: | 600*600mm |
| Panel Thickness: | 30/32/35/38/40mm |
| Finish Covering: | 1.0-2.0mm Anti-static Laminate HPL、2.0-3.0mm PVC、10mm Cermic、Marble、Granite、Nature Wood and etc. |
| Under Covering: | Bare、0.3-2.0mm Galvanized steel、0.1-2.0mm Aluminum Foil |
| Installation: | With Stringer System |

Characteristics:

- Non-combustible material;

- High dimensional precision: Tolerance of panel size is 0-0.40mm; Tolerance

of panel thickness is ±0.30mm; Un-flatness is ≤0.60mm;

- The load performance is strong, and the anti-static performance is excellent.

- Convenient removing, long performance life.

- Compared to other floors with the same advantages of a lightweight, like wood

core raised floor, Aluminum Honeycomb Floor’s capability of fire prevention and

anti-corrosive is superior.

- OEM is available;

Applications:

Data Centers、Commercial Buildings、Educational Facilities、Clean Rooms、

Control Rooms、Libraries and places where require anti-static environment

or have many wires.

Specification:

| Type | Size | Concertrated Load Defleation≤2.5mm |  |  | Uniform Load | Ultimate Load | System Resistance |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | mm | LBS | KN | KG | KN/㎡ | KN | Ω |
| FS662 | 600*600 | 662 | 2.95 | 300 | 12.50 | 8.85 | 1.0x106-1.0x109 |
| FS800 |  | 800 | 3.56 | 363 | 16.10 | 10.68 |  |
| FS1000 |  | 1000 | 4.45 | 454 | 23.00 | 13.35 |  |
| FS1250 |  | 1250 | 5.56 | 567 | 33.00 | 16.68 |  |
| FS1500 |  | 1500 | 6.67 | 680 | 34.50 | 20.02 |  |
| FS2000 |  | 2000 | 8.90 | 906 | 46.00 | 26.70 |  |

双层和单层的区别

Understructures:

| Product name: | Round Head Pedestal |
| --- | --- |
| Suggested Height: | FFH100-600mm |
| Tube: | Φ21*22*25*28/1.5mm |
| Top plate: | 90*90*3.0mm |
| Base plate:: | 95*95*2.0mm |
| Threaded rod: | M18/20/22 |
| Threaded rod length: | 80mm/100mm and more |
| Surface: | Cold galvanizing Hot galvanizing Powder coated |

| Product name: | Heavy duty pedestal |
| --- | --- |
| Suggested Height: | FFH600-2000mm |
| Tube: | Φ32/45/48*1.5mm |
| Top plate: | 90*90*3.0mm |
| Base plate:: | 95*95*3.0mm |
| Threaded rod: | M18 |
| Threaded rod length: | 80mm/100mm and more |
| Surface: | Cold galvanizing Hot galvanizing Powder coated |

| Product name: | Stringer |
| --- | --- |
| Size: | 540*31*22mm 1140*31*22mm |
| Steel thickness: | 1.0/1.2mm |
| Surface: | Cold galvanizing Hot galvanizing Powder coated |
| Gasket: | With |

Changzhou Abeite Computer Room Equipment Co.,Ltd

Add: No. 108, Chaoyang Village, Hengshanqiao Town, Wujin District,

Changzhou City, Jiangsu Province，China

Tel: +86(519)86056270

Fax: +86(519)86056270

E-mail: info@abeiteraisedfloor.com

Web: www. abeiteraisedfloor.com